## VPC Selection Table
VRG Controls - VPC Valve Pilot Controller Selection Matrix
Ver 0120318
Table 1.0 - VPC Selection Matrix
VPC MODEL | BOOSTER | PRIMARY INTERFACE | VOLUME | DISCH | APPLICATION | NOTES
VCP-SA-BV-ID |  | HPP or Other Pneumatic Positioner | N/A | ATM | Pipeline | Any ACTUATOR, Any DISCH
VCP-SA-BV-ID |  | RCV Research Control Valve | N/A | ATM | Pipeline
VCP-SA-BV-ID |  | VGP Positioner | N/A | ATM | Pipeline | Any ACTUATOR, Any DISCH
VPC-DA-BV |  | "Bettis" DA | Small | ATM | Pipeline
VPC-DA-BV |  | LHPA-DA | Small | ATM | Pipeline
VPC-DA-BV |  | RHPA-DA | Small | ATM | Pipeline
VPC-DA-SN | VBBIFOLD OR 4514AEI | "Bettis" DA | Large | ATM | Pipeline
VPC-DA-SN | VBBIFOLD OR 4514AEI | LHPA-DA | Large | ATM | Pipeline
VPC-DA-SN | VBBIFOLD OR 4514AEI | RHPA-DA | Large | ATM | Pipeline
VPC-DA-SN | VBBIFOLD | LHPA-DA | Large | BP | Pipeline
VPC-DA-SN | NA | LHPA-DA | Small | BP | Pipeline
VPC-DA-SN | VBBIFOLD | RHPA-DA | Large | BP | Pipeline
VPC-DA-SN | NA | RHPA-DA | Small | BP | Pipeline
VPC-DA-SN | VBBIFOLD OR 4514AEI | "Bettis" DA | Small | ATM | Power Plant
VCP-SA-BV-ID | VBBIFOLD OR 4514AEI | "Bettis" SR | Large | ATM | Power Plant
VCP-SA-BV-ID | VBBIFOLD OR 4514AEI | "Bettis" SR | Small | ATM | Power Plant
VPC-DA-SN | VBBIFOLD OR 4514AEI | RHPA-DA | Large | ATM | Power Plant
VPC-DA-SN | VBBIFOLD OR 4514AEI | RHPA-DA | Small | ATM | Power Plant | 6.0 in PRCV and Larger
VPC-DA-SN | VBBIFOLD | RHPA-DA | Large | BP | Power Plant
VPC-DA-SN | VBBIFOLD | RHPA-DA | Small | BP | Power Plant
VPC-DA-SN | NA | RHPA-DA | Small | BP | Power Plant | 4.0 in PRCV and Smaller
VPC-SA-BV |  | LD (667, 657) | Large | ATM | Pipeline
VPC-SA-BV |  | LHPA-SR | All | ATM | Pipeline
VPC-SA-BV |  | RD (1051, 1052) | All | ATM | Pipeline
VPC-SA-BV |  | RHPA-SR | Small | ATM | Pipeline
VPC-SA-BV |  | LHPA-SR | All | BP | Pipeline
VPC-SA-BV |  | RHPA-SR | Small | BP | Pipeline
VCP-SA-BV-ID |  | LD (667, 657) | Small | ATM | Pipeline
VCP-SA-BV-ID | VBBIFOLD, 4514AEI | RHPA-SR | Large | ATM | Pipeline
VCP-SA-BV-ID | VBBIFOLD | RHPA-SR | Large | BP | Pipeline
VCP-SA-BV-ID | VBBIFOLD, 4514AEI | RHPA-SR | Large | ATM | Power Plant
VCP-SA-BV-ID | VBBIFOLD, 4514AEI | RHPA-SR | Small | ATM | Power Plant
VCP-SA-BV-ID | VBBIFOLD | RHPA-SR | Large | BP | Power Plant
VCP-SA-BV-ID | VBBIFOLD | RHPA-SR | Small | BP | Power Plant
VRG Controls LLC
1199 Flex Court, Unit B ● Lake Zurich, Illinois 60047 USA
www.vrgcontrols.com ● email: sales@vrgcontrols.com

## GAP Controller Selection
VPC-SA-BV-GAP "GAP CONTROLLER" Configuration Summary
App | P Supply | Actautor Logic | Valve Normal Position | TRIGGER Valve Action | Latch (Y/N) | Normal State VERSA Signal | VPC-SA-BV-GAP Action | Versa Valve Model8
1 | ≥ 40 psig | DOUBLE ACTING | OPEN | CLOSE ON INCREASE SENSING PRESSURE | NO | Pressurized | REVERSE ACTING | VSP-4302-NGST VSP-4302-316-NGST6
2 | ≥ 40 psig | DOUBLE ACTING | OPEN | CLOSE ON INCREASE SENSING PRESSURE | YES | Pressurized | REVERSE ACTING | VSP-4302-NGST-181D VSP-4302-NGST-316-181D6
3 | ≥ 40 psig | DOUBLE ACTING | CLOSE | OPEN ON DECREASE SENSING PRESSURE | NO | Pressurized | DIRECT ACTING | VSP-4302-NGST VSP-4302-316-NGST6
4 | ≥ 40 psig | DOUBLE ACTING | CLOSE | OPEN ON DECREASE SENSING PRESSURE | YES | Pressurized | DIRECT ACTING | VSP-4302-NGST-181D VSP-4302-NGST-316-181D6
5 | ≥ 40 psig | SR – CLOSE | OPEN | CLOSE ON INCREASE SENSING PRESSURE | NO | Pressurized | REVERSE ACTING | VSP-3301-NGST VSP-3301-316-NGST8
6 | ≥ 40 psig | SR – CLOSE | OPEN | CLOSE ON INCREASE SENSING PRESSURE | YES | Pressurized | REVERSE ACTING | VSP-3301-NGST-181D VSP-3301-NGST-316-181D6
7 | ≥ 40 psig | SR – OPEN | CLOSE | OPEN ON DECREASE SENSING PRESSURE | NO | Pressurized | DIRECT ACTING | VSP-3301-NGST VSP-3301-316-NGST6
8 | ≥ 40 psig | SR – OPEN | CLOSE | OPEN ON DECREASE SENSING PRESSURE | YES | Pressurized | DIRECT ACTING | VSP-3301-NGST-181D VSP-3301-NGST-316-181D6
9 | < 40 psig | SR – CLOSE | OPEN | CLOSE ON INCREASE SENSING PRESSURE | NO | Pressurized | REVERSE ACTING | VSW-3301-NGST VSW-3301-316-NGST6
10 | < 40 psig | SR – CLOSE | OPEN | CLOSE ON INCREASE SENSING PRESSURE | YES | Pressurized | REVERSE ACTING | VSW-3301-NGST-181D VSW-3301-NGST-316-181D6
11 | < 40 psig | SR – OPEN | CLOSE | OPEN ON DECREASE SENSING PRESSURE | NO | Pressurized | DIRECT ACTING | VSW-3301-NGST VSW-3301-316-NGST6
12 | < 40 psig | SR – OPEN | CLOSE | OPEN ON DECREASE SENSING PRESSURE | NO | Pressurized | DIRECT ACTING | VSW-3301-NGST-181D VSW-3301-NGST-316-181D6
Notes: 1. PSUPPLY – Power Supply Gas necessary to load actuator 2. DOUBLE ACTING – Typical Piston Type Actuator Pressure to Close and Pressure to Open 3. SR-OPEN – Spring Return Actuator Fail (Spring) to OPEN on Loss Supply 4. SR-CLOSE – Spring Return Actuator Fail (Spring) to CLOSE on Loss Supply 5. When LATCH is applied, Versa Valve must be manually reset and Secondary 6. Standard construction of VERSA valves are BRASS. To upgrade to 316 Stainless Steel VERSA construction, designate with “316” within VERSA Model Number.
VER 041420

## SP 3W Sensor Selection
SP Series 3-Way Sensor Configuration Summary
App | P Supply | Actautor Logic | Valve Normal Position | TRIGGER Valve Action | Latch (Y/N) | Normal State VERSA Signal | SP 3-Way Sensor | Versa Valve Model8
1 | ≥ 40 psig | DOUBLE ACTING | OPEN | CLOSE ON INCREASE SENSING PRESSURE | NO | Pressurized | SPBOS3WNC | VSP-4302-NGST VSP-4302-316-NGST6
2 | ≥ 40 psig | DOUBLE ACTING | OPEN | CLOSE ON INCREASE SENSING PRESSURE | YES | Pressurized | SPBOS3WNC | VSP-4302-NGST-181D VSP-4302-NGST-316-181D6
3 | ≥ 40 psig | DOUBLE ACTING | CLOSE | OPEN ON DECREASE SENSING PRESSURE | NO | Pressurized | SPBOS3WNO | VSP-4302-NGST VSP-4302-316-NGST6
4 | ≥ 40 psig | DOUBLE ACTING | CLOSE | OPEN ON DECREASE SENSING PRESSURE | YES | Pressurized | SPBOS3WNO | VSP-4302-NGST-181D VSP-4302-NGST-316-181D6
5 | ≥ 40 psig | SR – CLOSE | OPEN | CLOSE ON INCREASE SENSING PRESSURE | NO | Pressurized | SPBOS3WNC | VSP-3301-NGST VSP-3301-316-NGST8
6 | ≥ 40 psig | SR – CLOSE | OPEN | CLOSE ON INCREASE SENSING PRESSURE | YES | Pressurized | SPBOS3WNC | VSP-3301-NGST-181D VSP-3301-NGST-316-181D6
7 | ≥ 40 psig | SR – OPEN | CLOSE | OPEN ON DECREASE SENSING PRESSURE | NO | Pressurized | SPBOS3WNO | VSP-3301-NGST VSP-3301-316-NGST6
8 | ≥ 40 psig | SR – OPEN | CLOSE | OPEN ON DECREASE SENSING PRESSURE | YES | Pressurized | SPBOS3WNO | VSP-3301-NGST-181D VSP-3301-NGST-316-181D6
9 | < 40 psig | SR – CLOSE | OPEN | CLOSE ON INCREASE SENSING PRESSURE | NO | Pressurized | SPBOS3WNC | VSW-3301-NGST VSW-3301-316-NGST6
10 | < 40 psig | SR – CLOSE | OPEN | CLOSE ON INCREASE SENSING PRESSURE | YES | Pressurized | SPBOS3WNC | VSW-3301-NGST-181D VSW-3301-NGST-316-181D6
11 | < 40 psig | SR – OPEN | CLOSE | OPEN ON DECREASE SENSING PRESSURE | NO | Pressurized | SPBOS3WNO | VSW-3301-NGST VSW-3301-316-NGST6
12 | < 40 psig | SR – OPEN | CLOSE | OPEN ON DECREASE SENSING PRESSURE | NO | Pressurized | SPBOS3WNO | VSW-3301-NGST-181D VSW-3301-NGST-316-181D6
Notes: 1. PSUPPLY – Power Supply Gas necessary to load actuator 2. DOUBLE ACTING – Typical Piston Type Actuator Pressure to Close and Pressure to Open 3. SR-OPEN – Spring Return Actuator Fail (Spring) to OPEN on Loss Supply 4. SR-CLOSE – Spring Return Actuator Fail (Spring) to CLOSE on Loss Supply 5. When LATCH is applied, Versa Valve must be manually reset and Secondary 6. Standard construction of VERSA valves are BRASS. To upgrade to 316 Stainless Steel VERSA construction, designate with “316” within VERSA Model Number.
VER 041420

## VGP Selection Table
VRG Controls - VGP Valve Gas Positioner Selection Matrix
Ver 0120318
Table 2.0 - VGP Selection Matrix
VPC MODEL | BOOSTER | PRIMARY INTERFACE | VOLUME | DISCH | APPLICATION | NOTES
VGP-DA-BV |  | RHPA-DA | Small | ATM | Pipeline
VGP-DA-SN | VBBIFOLD, 4514AEI | RHPA-DA | Large | ATM | Pipeline
VGP-DA-SN |  | RHPA-DA | Small | BP | Pipeline
VGP-DA-SN | VBBIFOLD | RHPA-DA | Large | BP | Pipeline
VGP-DA-BV |  | RHPA-DA | Small | ATM | Power Plant
VGP-DA-SN | VBBIFOLD, 4514AEI | RHPA-DA | Large | ATM | Power Plant
VGP-DA-SN |  | RHPA-DA | Small | BP | Power Plant
VGP-DA-SN | VBBIFOLD | RHPA-DA | Large | BP | Power Plant
VGP-DA-BV |  | LHPA-DA | Small | ATM | Pipeline
VGP-DA-SN | VBBIFOLD, 4514AEI | LHPA-DA | Large | ATM | Pipeline
VGP-DA-SN |  | LHPA-DA | Small | BP | Pipeline
VGP-DA-SN | VBBIFOLD | LHPA-DA | Large | BP | Pipeline
VGP-DA-BV |  | LHPA-DA | Small | ATM | Power Plant
VGP-DA-SN | VBBIFOLD, 4514AEI | LHPA-DA | Large | ATM | Power Plant
VGP-DA-SN |  | LHPA-DA | Small | BP | Power Plant
VGP-DA-SN | VBBIFOLD | LHPA-DA | Large | BP | Power Plant
VGP-SA-BV |  | RHPA-SR | Small | ATM | Pipeline
VGP-SA-BV | VBBIFOLD, 4514AEI | RHPA-SR | Large | ATM | Pipeline
VGP-SA-BV |  | RHPA-SR | Small | BP | Pipeline
VGP-SA-BV | VBBIFOLD | RHPA-SR | Large | BP | Pipeline
VGP-SA-BV |  | RHPA-SR | Small | ATM | Power Plant
VGP-SA-BV | VBBIFOLD, 4514AEI | RHPA-SR | Large | ATM | Power Plant
VGP-SA-BV |  | RHPA-SR | Small | BP | Power Plant
VGP-SA-BV | VBBIFOLD | RHPA-SR | Large | BP | Power Plant
VGP-SA-BV |  | LHPA-SR | Small | ATM | Pipeline
VGP-SA-BV | VBBIFOLD, 4514AEI | LHPA-SR | Large | ATM | Pipeline
VGP-SA-BV |  | LHPA-SR | Small | BP | Pipeline
VGP-SA-BV | VBBIFOLD | LHPA-SR | Large | BP | Pipeline
VGP-SA-BV |  | LHPA-SR | Small | ATM | Power Plant
VGP-SA-BV | VBBIFOLD, 4514AEI | LHPA-SR | Large | ATM | Power Plant
VGP-SA-BV |  | LHPA-SR | Small | BP | Power Plant
VGP-SA-BV | VBBIFOLD | LHPA-SR | Large | BP | Power Plant
VGP-SA-BV |  | LD (657, 667) | All Sizes | ATM | Pipeline
VGP-SA-BV |  | LD (657, 667) | All Sizes | ATM | Power Plant
VGP-DA-BV |  | FISHER 585 DA | Small | ATM | Pipeline
VGP-DA-SN | VBBIFOLD, 4514AEI | FISHER 585 DA | Large | ATM | Pipeline
VGP-DA-SN |  | FISHER 585 DA | Small | BP | Pipeline
VGP-DA-SN | VBBIFOLD | FISHER 585 DA | Large | BP | Pipeline
VGP-DA-BV |  | FISHER 585 DA | Small | ATM | Power Plant
VGP-DA-SN | VBBIFOLD, 4514AEI | FISHER 585 DA | Large | ATM | Power Plant
VGP-DA-SN |  | FISHER 585 DA | Small | BP | Power Plant
VGP-DA-SN | VBBIFOLD | FISHER 585 DA | Large | BP | Power Plant
VGP-SA-BV |  | FISHER 585 SR | Small | ATM | Pipeline
VGP-SA-BV | VBBIFOLD, 4514AEI | FISHER 585 SR | Large | ATM | Pipeline
VGP-SA-BV |  | FISHER 585 SR | Small | BP | Pipeline
VGP-SA-BV | VBBIFOLD | FISHER 585 SR | Large | BP | Pipeline
VGP-SA-BV |  | FISHER 585 SR | Small | ATM | Power Plant
VGP-SA-BV | VBBIFOLD, 4514AEI | FISHER 585 SR | Large | ATM | Power Plant
VGP-SA-BV |  | FISHER 585 SR | Small | BP | Power Plant
VGP-SA-BV | VBBIFOLD | FISHER 585 SR | Large | BP | Power Plant
VRG Controls LLC
1199 Flex Court, Unit B ● Lake Zurich, Illinois 60047 USA
www.vrgcontrols.com ● email: sales@vrgcontrols.com

## RCVC Selection Table
VRG Controls - RCVC Red Circle Valve Controller Selection Matrix
ver 022820
Table 3.0 - RCVC Selection Matrix
RCVC MODEL (1) | SOLENOIDS (X) | PRIMARY INTERFACE (2) | SUPPLY GAS (3) | VOLUME (4) | DISCH (5) | APPLICATION (6) | OTHER | Notes
RCVC | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Small | ATM | Pipeline | ADJUST ORF (2) | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Small | ATM | Pipeline | ADJUST ORF (1) | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Small | ATM | Pipeline | ADJUST ORF (2) | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Small | ATM | Pipeline | ADJUST ORF (1) | Requires Balluff
RCVC | EF8262H230A (2) - RCVCSOLSALO | LD (657, 667) | ≤ 50 psig | Small | ATM | Pipeline | ADJUST ORF (1) | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Small | BP | Pipeline | ADJUST ORF (2) | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Small | BP | Pipeline | ADJUST ORF (1) | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Small | BP | Pipeline | ADJUST ORF (2) | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Small | BP | Pipeline | ADJUST ORF (1) | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Small | ATM | Power Plant | ADJUST ORF (2) | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Small | ATM | Power Plant | ADJUST ORF (1) | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Small | ATM | Power Plant | ADJUST ORF (2) | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Small | ATM | Power Plant | ADJUST ORF (1) | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Small | BP | Power Plant | ADJUST ORF (2) | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Small | BP | Power Plant | ADJUST ORF (1) | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Small | BP | Power Plant | ADJUST ORF (2) | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Small | BP | Power Plant | ADJUST ORF (1) | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Large | ATM | Pipeline |  | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Large | ATM | Pipeline |  | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Large | ATM | Pipeline |  | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Large | ATM | Pipeline |  | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Large | BP | Pipeline |  | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Large | BP | Pipeline |  | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Large | BP | Pipeline |  | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Large | BP | Pipeline |  | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Large | ATM | Power Plant |  | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Large | ATM | Power Plant |  | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Large | ATM | Power Plant |  | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Large | ATM | Power Plant |  | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Large | BP | Power Plant |  | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Large | BP | Power Plant |  | Requires Balluff
RCVC | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Large | BP | Power Plant |  | Requires Balluff
RCVC | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Large | BP | Power Plant |  | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Small | ATM | Pipeline | ADJUST ORF (2) | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Small | ATM | Pipeline | ADJUST ORF (2) | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Small | BP | Pipeline | ADJUST ORF (2) | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Small | BP | Pipeline | ADJUST ORF (2) | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Small | ATM | Power Plant | ADJUST ORF (2) | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Small | ATM | Power Plant | ADJUST ORF (2) | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Small | BP | Power Plant | ADJUST ORF (2) | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Small | BP | Power Plant | ADJUST ORF (2) | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Large | ATM | Pipeline |  | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Large | ATM | Pipeline |  | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Large | BP | Pipeline |  | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Large | BP | Pipeline |  | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Large | ATM | Power Plant |  | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Large | ATM | Power Plant |  | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Large | BP | Power Plant |  | Requires Balluff
RCVC | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Large | BP | Power Plant |  | Requires Balluff
RCVC-REM | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Small | ATM | Pipeline | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Small | ATM | Pipeline | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Small | ATM | Pipeline | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Small | ATM | Pipeline | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | EF8262H230A (2) - RCVCSOLSALO | LD (657, 667) | ≤ 50 psig | Small | ATM | Pipeline | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Small | BP | Pipeline | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Small | BP | Pipeline | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Small | BP | Pipeline | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Small | BP | Pipeline | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Small | ATM | Power Plant | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Small | ATM | Power Plant | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Small | ATM | Power Plant | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Small | ATM | Power Plant | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Small | BP | Power Plant | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Small | BP | Power Plant | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Small | BP | Power Plant | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Small | BP | Power Plant | ADJUST ORF (1) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Large | ATM | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Large | ATM | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Large | ATM | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Large | ATM | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Large | BP | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Large | BP | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Large | BP | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Large | BP | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Large | ATM | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Large | ATM | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Large | ATM | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Large | ATM | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | RHPA-DA | 50-150 psig | Large | BP | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | RHPA-SR | > 50 psig | Large | BP | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4X (RCVCSOLDA) | LHPA-DA | 50-150 psig | Large | BP | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | ASCO EV8327G052 (2) - RCVCSOLSAHI | LHPA-SR | > 50 psig | Large | BP | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Small | ATM | Pipeline | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Small | ATM | Pipeline | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Small | BP | Pipeline | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Small | BP | Pipeline | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Small | ATM | Power Plant | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Small | ATM | Power Plant | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Small | BP | Power Plant | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Small | BP | Power Plant | ADJUST ORF (2) | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Large | ATM | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Large | ATM | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Large | BP | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Large | BP | Pipeline |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Large | ATM | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Large | ATM | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | RHPA-DA | 151 - 250 psig | Large | BP | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC-REM | AAA SY4XZ (RCVCSOLDAHI) | LHPA-DA | 151 - 250 psig | Large | BP | Power Plant |  | Requires Balluff, RCVCREMJUNC
RCVC | EF8262H230A (2) - RCVCSOLSALO | RD (1051, 1052) | ≤ 50 psig | Small | ATM | Pipeline | ADJUST ORF (1) | Requires Rotary Feedback
RCVC-REM | EF8262H230A (2) - RCVCSOLSALO | RD (1051, 1052) | ≤ 50 psig | Small | ATM | Pipeline | ADJUST ORF (1) | Requires Rotary Feedback, RCVCREMJUNC
VRG Controls LLC
1199 Flex Court, Unit B ● Lake Zurich, Illinois 60047 USA
www.vrgcontrols.com ● email: sales@vrgcontrols.com

## Orifice Selection
VRG Controls - Adjustable Orifice Selection Matrix
ver 032320
Table 4.0 - Orifice Selection Matrix
PRIMARY | BOOSTER | PRIMARY INTERFACE | VOLUME | DISCH | APPLICATION | OPEN | CLOSE | ID / OTHER | SUPPLY | NOTES
VPC-DA-BV |  | RHPA-DA | Small | ATM | Pipeline | S | S | N/A
VPC-DA-SN |  | RHPA-DA | Small | ATM | Pipeline | S | S | N/A
VPC-DA-SN |  | RHPA-DA | Small | BP |  | M | M | N/A |  | REQUIRES DN EX MANIFOLD
VPC-DA-SN | VBBIFOLD, 4514AEI | RHPA-DA | Small | ATM |  | S | S | N/A
VPC-DA-SN | VBBIFOLD, 4514AEI | RHPA-DA | Large | ATM |  | S | S | N/A
VPC-DA-SN | VBBIFOLD | RHPA-DA | Small | BP |  | S | S | N/A
VPC-DA-SN | VBBIFOLD | RHPA-DA | Large | BP |  | S | S | N/A
VPC-SA-BV-ID |  | LD | Small | ATM |  | S | S | S | ≤ 50 PSIG
VPC-SA-BV |  | LD | Large | ATM | Pipeline | M | M | N/A | ≤ 50 PSIG
VPC-SA-BV |  | LHPA-SR | Small | ATM | Pipeline | L | L | N/A | > 50 PSIG
VPC-SA-BV |  | RHPA-SR | Small | ATM | Pipeline | L | L | N/A | > 50 PSIG
VPC-SA-BV-ID | VBBIFOLD, 4514AEI | LD | Large | ATM |  | S | S | S
VPC-SA-BV-ID | VBBIFOLD, 4514AEI | LHPA-SR | Small | ATM |  | S | S | S
VPC-SA-BV-ID |  | LHPA-SR | Small | BP |  | S | S | S
VPC-SA-BV-ID | VBBIFOLD, 4514AEI | LHPA-SR | Large | ATM |  | S | S | S
VPC-SA-BV-ID | VBBIFOLD, 4514AEI | RHPA-SR | Small | ATM |  | S | S | S
VPC-SA-BV-ID | VBBIFOLD, 4514AEI | RHPA-SR | Large | ATM |  | S | S | S
VPC-SA-BV-ID |  | LHPA-SR | Small | ATM |  | L | L | S
VPC-SA-BV-ID |  | RHPA-SR | Small | ATM |  | L | L | S
VPC-SA-BV-ID |  | VGP (ALL MODELS) | All | ATM |  | S | S | S |  | 3-15 psig, 6-30 psig or similar loading, REQUIRES DN EX MANIFOLD
VPC-SA-BV-ID |  | HPP or Other Pneumatic Positioner | All | ATM |  | S | S | S |  | 3-15 psig, 6-30 psig or similar loading
VPC-SA-BV-ID |  | BADGER RCV | All | ATM |  | S | S | S |  | 3-15 psig, 6-30 psig, “Droopless” Control
VGP-DA-BV |  | RHPA-DA | Small | ATM |  | S | S | N/A
VGP-DA-BV |  | LHPA-DA | Small | ATM |  | S | S | N/A
VGP-DA-SN |  | RHPA-DA | Small | BP |  | S | S | N/A |  | Must Install VPCDSDISCH Manifold
VGP-DA-SN |  | LHPA-DA | Small | BP |  | S | S | N/A |  | Must Install VPCDSDISCH Manifold
VGP-DA-SN |  | RHPA-DA | Large | ATM |  | S | S | N/A
VGP-DA-SN |  | LHPA-DA | Large | ATM |  | S | S | N/A
VGP-DA-SN | VBBIFOLD | RHPA-DA | Large | BP |  | S | S | N/A |  | Must Install VPCDSDISCH Manifold
VGP-DA-SN | VBBIFOLD | LHPA-DA | Large | BP |  | S | S | N/A |  | Must Install VPCDSDISCH Manifold
VGP-SA-BV |  | RHPA-SR | Small | ATM |  | N/A | N/A | N/A
VGP-SA-BV |  | LHPA-SR | Small | ATM |  | N/A | N/A | N/A
VGP-SA-BV | VBBIFOLD, 4514AEI | RHPA-SR | Large | ATM |  | N/A | N/A | N/A
VGP-SA-BV | VBBIFOLD, 4514AEI | LHPA-SR | Large | ATM |  | N/A | N/A | N/A
VGP-SA-BV |  | RHPA-SR | Small | BP |  | N/A | N/A | N/A
VGP-SA-BV |  | LHPA-SR | Small | BP |  | N/A | N/A | N/A
VGP-SA-BV | VBBIFOLD | RHPA-SR | Large | BP |  | N/A | N/A | N/A
VGP-SA-BV | VBBIFOLD | LHPA-SR | Large | BP |  | N/A | N/A | N/A
VGP-SA-BV |  | LD | All | ATM |  | N/A | N/A | N/A
RCVC |  | RHPA-DA | Small | ATM |  | M | M | N/A
RCVC |  | LHPA-DA | Small | ATM |  | M | M | N/A
RCVC |  | RHPA-DA | Small | BP |  | M | M | N/A
RCVC |  | LHPA-DA | Small | BP |  | M | M | N/A
RCVC |  | RHPA-DA | Large | ATM |  | N/A | N/A | N/A
RCVC |  | LHPA-DA | Large | ATM |  | N/A | N/A | N/A
RCVC |  | RHPA-DA | Large | BP |  | N/A | N/A | N/A
RCVC |  | LHPA-DA | Large | BP |  | N/A | N/A | N/A
RCVC |  | RHPA-SR | Small | ATM |  | N/A | N/A | M |  | USE ONLY ONE (1) ADJ ORF ON EX SIDE
RCVC |  | LHPA-SR | Small | ATM |  | N/A | N/A | M |  | USE ONLY ONE (1) ADJ ORF ON EX SIDE
RCVC |  | RHPA-SR | Small | BP |  | N/A | N/A | M |  | USE ONLY ONE (1) ADJ ORF ON EX SIDE
RCVC |  | LHPA-SR | Small | BP |  | N/A | N/A | M |  | USE ONLY ONE (1) ADJ ORF ON EX SIDE
RCVC |  | RHPA-SR | Large | ATM |  | N/A | N/A | N/A
RCVC |  | LHPA-SR | Large | ATM |  | N/A | N/A | N/A
RCVC |  | RHPA-SR | Large | BP |  | N/A | N/A | N/A
RCVC |  | LHPA-SR | Large | BP |  | N/A | N/A | N/A
SENSORS (ALL) |  | VARIOUS | All | ATM |  | N/A | N/A | S |  | USE ONLY ONE (1) ADJ ORF
RP PILOTS (ALL) |  | MOONEY OR SIMILAR | All | BP |  | N/A | N/A | S |  | USE ONLY ONE (1) ADJ ORF
RCVC |  | LD | All | ATM |  | N/A | N/A | M |  | USE ONLY ONE (1) ADJ ORF ON EX SIDE
VRG Controls LLC
1199 Flex Court, Unit B ● Lake Zurich, Illinois 60047 USA
www.vrgcontrols.com ● email: sales@vrgcontrols.com

## RHPA Selection
VRG Controls - VPC Valve Pilot Controller Selection Matrix
Ver 0120318
Table 5.0 - RHPA Selection Matrix
PRCV Size | Actuator Action | Low Ambient Temp. | Eff. Supply Gas | Max Control Differential | PRCV Actuator Size
2" (50mm) | SPRING CLOSED | -20 F | 90 psig | 500 psid | 6X4SR10
3" (80mm) | SPRING CLOSED | -20 F | 90 psig | 500 psid | 6X6SR20
4" (100mm) | SPRING CLOSED | -20 F | 90 psig | 500 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | -20 F | 90 psig | 500 psid | 10X8SR40
8" (200mm) | SPRING CLOSED | -20 F | 90 psig | 500 psid | 12X12SR50/20
10" (250mm) | SPRING CLOSED | -20 F | 90 psig | 500 psid | 14X12SR60/40
12" (300mm) | SPRING CLOSED | -20 F | 90 psig | 500 psid | D12x12SRD50/20
2" (50mm) | SPRING CLOSED | -20 F | 90 psig | 1000 psid | 6X4SR10
3" (80mm) | SPRING CLOSED | -20 F | 90 psig | 1000 psid | 8X6SR20
4" (100mm) | SPRING CLOSED | -20 F | 90 psig | 1000 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | -20 F | 90 psig | 1000 psid | 10X12SR40
8" (200mm) | SPRING CLOSED | -20 F | 90 psig | 1000 psid | 12X12SR60
10" (250mm) | SPRING CLOSED | -20 F | 90 psig | 1000 psid | 12X12/10X12SR50/20/50
12" (300mm) | SPRING CLOSED | -20 F | 90 psig | 1000 psid | 12X13/14X14SR60/60/40
2" (50mm) | SPRING CLOSED | -20 F | 90 psig | 1500 psid | 6X6SR20
3" (80mm) | SPRING CLOSED | -20 F | 90 psig | 1500 psid | 8X6SR30
4" (100mm) | SPRING CLOSED | -20 F | 90 psig | 1500 psid | 8X8SR30
6" (150mm) | SPRING CLOSED | -20 F | 90 psig | 1500 psid | 10X12SR50
8" (200mm) | SPRING CLOSED | -20 F | 90 psig | 1500 psid | 14X12SR60/40
10" (250mm) | SPRING CLOSED | -20 F | 90 psig | 1500 psid | D12x12SRD50/20
12" (300mm) | SPRING CLOSED | -20 F | 90 psig | 1500 psid | 14x13/14X14SRD60/40
2" (50mm) | SPRING OPEN | -20 F | 90 psig | 500 psid | 6X4SR10
3" (80mm) | SPRING OPEN | -20 F | 90 psig | 500 psid | 6X6SR20
4" (100mm) | SPRING OPEN | -20 F | 90 psig | 500 psid | 8X6SR30
6" (150mm) | SPRING OPEN | -20 F | 90 psig | 500 psid | 10X6SR40
8" (200mm) | SPRING OPEN | -20 F | 90 psig | 500 psid | 12X12SR50
10" (250mm) | SPRING OPEN | -20 F | 90 psig | 500 psid | 12X12SR50
12" (300mm) | SPRING OPEN | -20 F | 90 psig | 500 psid | 10x12/12x12SRD50
2" (50mm) | SPRING OPEN | -20 F | 90 psig | 1000 psid | 6X4SR10
3" (80mm) | SPRING OPEN | -20 F | 90 psig | 1000 psid | 8X6SR20
4" (100mm) | SPRING OPEN | -20 F | 90 psig | 1000 psid | 8X6SR30
6" (150mm) | SPRING OPEN | -20 F | 90 psig | 1000 psid | 10X8SR40
8" (200mm) | SPRING OPEN | -20 F | 90 psig | 1000 psid | 12X12SR50
10" (250mm) | SPRING OPEN | -20 F | 90 psig | 1000 psid | 14X12SR50/20
12" (300mm) | SPRING OPEN | -20 F | 90 psig | 1000 psid | 10x12/12x12SRD50
2" (50mm) | SPRING OPEN | -20 F | 90 psig | 1500 psid | 6X6SR20
3" (80mm) | SPRING OPEN | -20 F | 90 psig | 1500 psid | 8X6SR30
4" (100mm) | SPRING OPEN | -20 F | 90 psig | 1500 psid | 8X8SR30
6" (150mm) | SPRING OPEN | -20 F | 90 psig | 1500 psid | 10X12SR40
8" (200mm) | SPRING OPEN | -20 F | 90 psig | 1500 psid | 12X12SR60
10" (250mm) | SPRING OPEN | -20 F | 90 psig | 1500 psid | 14X12SR50/20
12" (300mm) | SPRING OPEN | -20 F | 90 psig | 1500 psid | D12X12SRD50
2" (50mm) | SPRING CLOSED | +20 F | 90 psig | 500 psid | 5X4SR10
3" (80mm) | SPRING CLOSED | +20 F | 90 psig | 500 psid | 6X6SR20
4" (100mm) | SPRING CLOSED | +20 F | 90 psig | 500 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | +20 F | 90 psig | 500 psid | 10X6SR40
8" (200mm) | SPRING CLOSED | +20 F | 90 psig | 500 psid | 12X12SR50/20
10" (250mm) | SPRING CLOSED | +20 F | 90 psig | 500 psid | 14x12SR60/30
12" (300mm) | SPRING CLOSED | +20 F | 90 psig | 500 psid | D12x12SRD50/20
2" (50mm) | SPRING CLOSED | +20 F | 90 psig | 1000 psid | 6X4SR10
3" (80mm) | SPRING CLOSED | +20 F | 90 psig | 1000 psid | 8X6SR20
4" (100mm) | SPRING CLOSED | +20 F | 90 psig | 1000 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | +20 F | 90 psig | 1000 psid | 10X8SR40
8" (200mm) | SPRING CLOSED | +20 F | 90 psig | 1000 psid | 12X12SR60
10" (250mm) | SPRING CLOSED | +20 F | 90 psig | 1000 psid | 12X12/10X12SR50/20/50
12" (300mm) | SPRING CLOSED | +20 F | 90 psig | 1000 psid | 12X13/14X14SR60/60/40
2" (50mm) | SPRING CLOSED | +20 F | 90 psig | 1500 psid | 6X6SR20
3" (80mm) | SPRING CLOSED | +20 F | 90 psig | 1500 psid | 8X6SR30
4" (100mm) | SPRING CLOSED | +20 F | 90 psig | 1500 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | +20 F | 90 psig | 1500 psid | 10X8SR50
8" (200mm) | SPRING CLOSED | +20 F | 90 psig | 1500 psid | 14X12SR60/40
10" (250mm) | SPRING CLOSED | +20 F | 90 psig | 1500 psid | D12x12SRD50/20
12" (300mm) | SPRING CLOSED | +20 F | 90 psig | 1500 psid | 14x13/14X14SRD60/40
2" (50mm) | SPRING OPEN | +20 F | 90 psig | 500 psid | 5X4SR10
3" (80mm) | SPRING OPEN | +20 F | 90 psig | 500 psid | 6X6SR20
4" (100mm) | SPRING OPEN | +20 F | 90 psig | 500 psid | 8X6SR30
6" (150mm) | SPRING OPEN | +20 F | 90 psig | 500 psid | 10X6SR40
8" (200mm) | SPRING OPEN | +20 F | 90 psig | 500 psid | 12X12SR50
10" (250mm) | SPRING OPEN | +20 F | 90 psig | 500 psid | 12X12SR50
12" (300mm) | SPRING OPEN | +20 F | 90 psig | 500 psid | 10x12/12x12SRD50
2" (50mm) | SPRING OPEN | +20 F | 90 psig | 1000 psid | 6X4SR10
3" (80mm) | SPRING OPEN | +20 F | 90 psig | 1000 psid | 8X6SR20
4" (100mm) | SPRING OPEN | +20 F | 90 psig | 1000 psid | 8X6SR30
6" (150mm) | SPRING OPEN | +20 F | 90 psig | 1000 psid | 10X6SR40
8" (200mm) | SPRING OPEN | +20 F | 90 psig | 1000 psid | 12X12SR50
10" (250mm) | SPRING OPEN | +20 F | 90 psig | 1000 psid | 14X12SR50/20
12" (300mm) | SPRING OPEN | +20 F | 90 psig | 1000 psid | 10x12/12x12SRD50
2" (50mm) | SPRING OPEN | +20 F | 90 psig | 1500 psid | 6X6SR20
3" (80mm) | SPRING OPEN | +20 F | 90 psig | 1500 psid | 8X6SR30
4" (100mm) | SPRING OPEN | +20 F | 90 psig | 1500 psid | 8X6SR30
6" (150mm) | SPRING OPEN | +20 F | 90 psig | 1500 psid | 10X8SR40
8" (200mm) | SPRING OPEN | +20 F | 90 psig | 1500 psid | 12X12SR50
10" (250mm) | SPRING OPEN | +20 F | 90 psig | 1500 psid | 14X12SR50/20
12" (300mm) | SPRING OPEN | +20 F | 90 psig | 1500 psid | D12X12SRD50
2" (50mm) | SPRING CLOSED | -20 F | 125 psig | 500 psid | 5X4SR10
3" (80mm) | SPRING CLOSED | -20 F | 125 psig | 500 psid | 6X6SR20
4" (100mm) | SPRING CLOSED | -20 F | 125 psig | 500 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | -20 F | 125 psig | 500 psid | 8X8SR40
8" (200mm) | SPRING CLOSED | -20 F | 125 psig | 500 psid | 10X12SR50
10" (250mm) | SPRING CLOSED | -20 F | 125 psig | 500 psid | 12X12SR60/40
12" (300mm) | SPRING CLOSED | -20 F | 125 psig | 500 psid | D10x12SRD50/20
2" (50mm) | SPRING CLOSED | -20 F | 125 psig | 1000 psid | 5X4SR10
3" (80mm) | SPRING CLOSED | -20 F | 125 psig | 1000 psid | 8X6SR20
4" (100mm) | SPRING CLOSED | -20 F | 125 psig | 1000 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | -20 F | 125 psig | 1000 psid | 8X8SR40
8" (200mm) | SPRING CLOSED | -20 F | 125 psig | 1000 psid | 10X12SR60
10" (250mm) | SPRING CLOSED | -20 F | 125 psig | 1000 psid | D10x12SRD50
12" (300mm) | SPRING CLOSED | -20 F | 125 psig | 1000 psid | 10X12/12x12SR50/20/60/40
2" (50mm) | SPRING CLOSED | -20 F | 125 psig | 1500 psid | 6X4SR20
3" (80mm) | SPRING CLOSED | -20 F | 125 psig | 1500 psid | 8X6SR30
4" (100mm) | SPRING CLOSED | -20 F | 125 psig | 1500 psid | 8X6SR40
6" (150mm) | SPRING CLOSED | -20 F | 125 psig | 1500 psid | 10X8SR39
8" (200mm) | SPRING CLOSED | -20 F | 125 psig | 1500 psid | 12X12SR60/40
10" (250mm) | SPRING CLOSED | -20 F | 125 psig | 1500 psid | 10X12/12x12SR50/60/40
12" (300mm) | SPRING CLOSED | -20 F | 125 psig | 1500 psid | 12X13/12X14SRD60/40
2" (50mm) | SPRING OPEN | -20 F | 125 psig | 500 psid | 5X4SR10
3" (80mm) | SPRING OPEN | -20 F | 125 psig | 500 psid | 6X6SR20
4" (100mm) | SPRING OPEN | -20 F | 125 psig | 500 psid | 8X6SR30
6" (150mm) | SPRING OPEN | -20 F | 125 psig | 500 psid | 8X8SR40
8" (200mm) | SPRING OPEN | -20 F | 125 psig | 500 psid | 10X12SR50
10" (250mm) | SPRING OPEN | -20 F | 125 psig | 500 psid | 10X12SR50
12" (300mm) | SPRING OPEN | -20 F | 125 psig | 500 psid | 12X12SR5020
2" (50mm) | SPRING OPEN | -20 F | 125 psig | 1000 psid | 5X4SR10
3" (80mm) | SPRING OPEN | -20 F | 125 psig | 1000 psid | 8X6SR20
4" (100mm) | SPRING OPEN | -20 F | 125 psig | 1000 psid | 8X6SR30
6" (150mm) | SPRING OPEN | -20 F | 125 psig | 1000 psid | 8X8SR40
8" (200mm) | SPRING OPEN | -20 F | 125 psig | 1000 psid | 10X12SR50
10" (250mm) | SPRING OPEN | -20 F | 125 psig | 1000 psid | 12X12SR60/40
12" (300mm) | SPRING OPEN | -20 F | 125 psig | 1000 psid | 14X12SR60/40
2" (50mm) | SPRING OPEN | -20 F | 125 psig | 1500 psid | 6X4SR20
3" (80mm) | SPRING OPEN | -20 F | 125 psig | 1500 psid | 8X6SR30
4" (100mm) | SPRING OPEN | -20 F | 125 psig | 1500 psid | 8X6SR30
6" (150mm) | SPRING OPEN | -20 F | 125 psig | 1500 psid | 10X8SR40
8" (200mm) | SPRING OPEN | -20 F | 125 psig | 1500 psid | 10X12SR60
10" (250mm) | SPRING OPEN | -20 F | 125 psig | 1500 psid | 14X12SR60/40
12" (300mm) | SPRING OPEN | -20 F | 125 psig | 1500 psid | D10x12SRD50
2" (50mm) | SPRING CLOSED | +20 F | 125 psig | 500 psid | 5X4SR10
3" (80mm) | SPRING CLOSED | +20 F | 125 psig | 500 psid | 6X6SR20
4" (100mm) | SPRING CLOSED | +20 F | 125 psig | 500 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | +20 F | 125 psig | 500 psid | 8X8SR40
8" (200mm) | SPRING CLOSED | +20 F | 125 psig | 500 psid | 10X12SR50
10" (250mm) | SPRING CLOSED | +20 F | 125 psig | 500 psid | 12X12SR60/40
12" (300mm) | SPRING CLOSED | +20 F | 125 psig | 500 psid | D10x12SRD50
2" (50mm) | SPRING CLOSED | +20 F | 125 psig | 1000 psid | 5X4SR10
3" (80mm) | SPRING CLOSED | +20 F | 125 psig | 1000 psid | 6X6SR20
4" (100mm) | SPRING CLOSED | +20 F | 125 psig | 1000 psid | 8X6SR30
6" (150mm) | SPRING CLOSED | +20 F | 125 psig | 1000 psid | 8X8SR40
8" (200mm) | SPRING CLOSED | +20 F | 125 psig | 1000 psid | 10X12SR50
10" (250mm) | SPRING CLOSED | +20 F | 125 psig | 1000 psid | 12X12SR60/40
12" (300mm) | SPRING CLOSED | +20 F | 125 psig | 1000 psid | 10X12/12x12SR50/20/60/40
2" (50mm) | SPRING CLOSED | +20 F | 125 psig | 1500 psid | 6X4SR20
3" (80mm) | SPRING CLOSED | +20 F | 125 psig | 1500 psid | 8X6SR30
4" (100mm) | SPRING CLOSED | +20 F | 125 psig | 1500 psid | 8X6SR40
6" (150mm) | SPRING CLOSED | +20 F | 125 psig | 1500 psid | 10X6SR50
8" (200mm) | SPRING CLOSED | +20 F | 125 psig | 1500 psid | 12X12SR60/40
10" (250mm) | SPRING CLOSED | +20 F | 125 psig | 1500 psid | D10x12SRD50
12" (300mm) | SPRING CLOSED | +20 F | 125 psig | 1500 psid | 12X13/12X14SRD60/40
2" (50mm) | SPRING OPEN | +20 F | 125 psig | 500 psid | 5X4SR10
3" (80mm) | SPRING OPEN | +20 F | 125 psig | 500 psid | 6X6SR20
4" (100mm) | SPRING OPEN | +20 F | 125 psig | 500 psid | 8X6SR30
6" (150mm) | SPRING OPEN | +20 F | 125 psig | 500 psid | 8X8SR40
8" (200mm) | SPRING OPEN | +20 F | 125 psig | 500 psid | 10X12SR50
10" (250mm) | SPRING OPEN | +20 F | 125 psig | 500 psid | 10X12SR50
12" (300mm) | SPRING OPEN | +20 F | 125 psig | 500 psid | 12X12SR50/20
2" (50mm) | SPRING OPEN | +20 F | 125 psig | 1000 psid | 5X4SR10
3" (80mm) | SPRING OPEN | +20 F | 125 psig | 1000 psid | 6X6SR20
4" (100mm) | SPRING OPEN | +20 F | 125 psig | 1000 psid | 8X6SR30
6" (150mm) | SPRING OPEN | +20 F | 125 psig | 1000 psid | 8X8SR40
8" (200mm) | SPRING OPEN | +20 F | 125 psig | 1000 psid | 10X12SR50
10" (250mm) | SPRING OPEN | +20 F | 125 psig | 1000 psid | 12X12SR60
12" (300mm) | SPRING OPEN | +20 F | 125 psig | 1000 psid | 14X12SR60/40
2" (50mm) | SPRING OPEN | +20 F | 125 psig | 1500 psid | 6X4SR20
3" (80mm) | SPRING OPEN | +20 F | 125 psig | 1500 psid | 6X6SR20
4" (100mm) | SPRING OPEN | +20 F | 125 psig | 1500 psid | 8X6SR30
6" (150mm) | SPRING OPEN | +20 F | 125 psig | 1500 psid | 10X6SR50
8" (200mm) | SPRING OPEN | +20 F | 125 psig | 1500 psid | 10X12SR50
10" (250mm) | SPRING OPEN | +20 F | 125 psig | 1500 psid | 14X12SR60/40
12" (300mm) | SPRING OPEN | +20 F | 125 psig | 1500 psid | D10x12SRD50
2" (50mm) | DOUBLE ACTING | -20 F | 90 psig | 500 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | -20 F | 90 psig | 500 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | -20 F | 90 psig | 500 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | -20 F | 90 psig | 500 psid | RHPA8X6DA
8" (200mm) | DOUBLE ACTING | -20 F | 90 psig | 500 psid | RHPA10X6DA
10" (250mm) | DOUBLE ACTING | -20 F | 90 psig | 500 psid | RHPA10X12DA
12" (300mm) | DOUBLE ACTING | -20 F | 90 psig | 500 psid | RHPA10X12DA
2" (50mm) | DOUBLE ACTING | -20 F | 90 psig | 1000 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | -20 F | 90 psig | 1000 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | -20 F | 90 psig | 1000 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | -20 F | 90 psig | 1000 psid | RHPA8X8DA
8" (200mm) | DOUBLE ACTING | -20 F | 90 psig | 1000 psid | RHPA10X8DA
10" (250mm) | DOUBLE ACTING | -20 F | 90 psig | 1000 psid | RHPA10X12DA
12" (300mm) | DOUBLE ACTING | -20 F | 90 psig | 1000 psid | RHPA12X12DA
2" (50mm) | DOUBLE ACTING | -20 F | 90 psig | 1500 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | -20 F | 90 psig | 1500 psid | RHPA6X4DA
4" (100mm) | DOUBLE ACTING | -20 F | 90 psig | 1500 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | -20 F | 90 psig | 1500 psid | RHPA8X8DA
8" (200mm) | DOUBLE ACTING | -20 F | 90 psig | 1500 psid | RHPA10X12DA
10" (250mm) | DOUBLE ACTING | -20 F | 90 psig | 1500 psid | RHPA12X12DA
12" (300mm) | DOUBLE ACTING | -20 F | 90 psig | 1500 psid | RHPA12X12DA
2" (50mm) | DOUBLE ACTING | +20 F | 90 psig | 500 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | +20 F | 90 psig | 500 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | +20 F | 90 psig | 500 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | +20 F | 90 psig | 500 psid | RHPA8X6DA
8" (200mm) | DOUBLE ACTING | +20 F | 90 psig | 500 psid | RHPA10X6DA
10" (250mm) | DOUBLE ACTING | +20 F | 90 psig | 500 psid | RHPA10X8DA
12" (300mm) | DOUBLE ACTING | +20 F | 90 psig | 500 psid | RHPA10X12DA
2" (50mm) | DOUBLE ACTING | +20 F | 90 psig | 1000 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | +20 F | 90 psig | 1000 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | +20 F | 90 psig | 1000 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | +20 F | 90 psig | 1000 psid | RHPA8X6DA
8" (200mm) | DOUBLE ACTING | +20 F | 90 psig | 1000 psid | RHPA10X8DA
10" (250mm) | DOUBLE ACTING | +20 F | 90 psig | 1000 psid | RHPA10X12DA
12" (300mm) | DOUBLE ACTING | +20 F | 90 psig | 1000 psid | RHPA12X12DA
2" (50mm) | DOUBLE ACTING | +20 F | 90 psig | 1500 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | +20 F | 90 psig | 1500 psid | RHPA6X4DA
4" (100mm) | DOUBLE ACTING | +20 F | 90 psig | 1500 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | +20 F | 90 psig | 1500 psid | RHPA8X8DA
8" (200mm) | DOUBLE ACTING | +20 F | 90 psig | 1500 psid | RHPA10X8DA
10" (250mm) | DOUBLE ACTING | +20 F | 90 psig | 1500 psid | RHPA10X12DA
12" (300mm) | DOUBLE ACTING | +20 F | 90 psig | 1500 psid | RHPA12X12DA
2" (50mm) | DOUBLE ACTING | -20 F | 125 psig | 500 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | -20 F | 125 psig | 500 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | -20 F | 125 psig | 500 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | -20 F | 125 psig | 500 psid | RHPA8X6DA
8" (200mm) | DOUBLE ACTING | -20 F | 125 psig | 500 psid | RHPA8X8DA
10" (250mm) | DOUBLE ACTING | -20 F | 125 psig | 500 psid | RHPA10X8DA
12" (300mm) | DOUBLE ACTING | -20 F | 125 psig | 500 psid | RHPA10X8DA
2" (50mm) | DOUBLE ACTING | -20 F | 125 psig | 1000 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | -20 F | 125 psig | 1000 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | -20 F | 125 psig | 1000 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | -20 F | 125 psig | 1000 psid | RHPA8X6DA
8" (200mm) | DOUBLE ACTING | -20 F | 125 psig | 1000 psid | RHPA10X6DA
10" (250mm) | DOUBLE ACTING | -20 F | 125 psig | 1000 psid | RHPA10X8DA
12" (300mm) | DOUBLE ACTING | -20 F | 125 psig | 1000 psid | RHPA10X12DA
2" (50mm) | DOUBLE ACTING | -20 F | 125 psig | 1500 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | -20 F | 125 psig | 1500 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | -20 F | 125 psig | 1500 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | -20 F | 125 psig | 1500 psid | RHPA8X8DA
8" (200mm) | DOUBLE ACTING | -20 F | 125 psig | 1500 psid | RHPA10X8DA
10" (250mm) | DOUBLE ACTING | -20 F | 125 psig | 1500 psid | RHPA10X12DA
12" (300mm) | DOUBLE ACTING | -20 F | 125 psig | 1500 psid | RHPA12X12DA
2" (50mm) | DOUBLE ACTING | +20 F | 125 psig | 500 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | +20 F | 125 psig | 500 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | +20 F | 125 psig | 500 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | +20 F | 125 psig | 500 psid | RHPA8X6DA
8" (200mm) | DOUBLE ACTING | +20 F | 125 psig | 500 psid | RHPA8X8DA
10" (250mm) | DOUBLE ACTING | +20 F | 125 psig | 500 psid | RHPA10X6DA
12" (300mm) | DOUBLE ACTING | +20 F | 125 psig | 500 psid | RHPA10X8DA
2" (50mm) | DOUBLE ACTING | +20 F | 125 psig | 1000 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | +20 F | 125 psig | 1000 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | +20 F | 125 psig | 1000 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | +20 F | 125 psig | 1000 psid | RHPA8X6DA
8" (200mm) | DOUBLE ACTING | +20 F | 125 psig | 1000 psid | RHPA10X6DA
10" (250mm) | DOUBLE ACTING | +20 F | 125 psig | 1000 psid | RHPA10X8DA
12" (300mm) | DOUBLE ACTING | +20 F | 125 psig | 1000 psid | RHPA10X12DA
2" (50mm) | DOUBLE ACTING | +20 F | 125 psig | 1500 psid | RHPA5X4DA
3" (80mm) | DOUBLE ACTING | +20 F | 125 psig | 1500 psid | RHPA5X4DA
4" (100mm) | DOUBLE ACTING | +20 F | 125 psig | 1500 psid | RHPA6X6DA
6" (150mm) | DOUBLE ACTING | +20 F | 125 psig | 1500 psid | RHPA8X6DA
8" (200mm) | DOUBLE ACTING | +20 F | 125 psig | 1500 psid | RHPA10X6DA
10" (250mm) | DOUBLE ACTING | +20 F | 125 psig | 1500 psid | RHPA10X12DA
12" (300mm) | DOUBLE ACTING | +20 F | 125 psig | 1500 psid | RHPA10X12DA
VRG Controls LLC
1199 Flex Court, Unit B ● Lake Zurich, Illinois 60047 USA
www.vrgcontrols.com ● email: sales@vrgcontrols.com