## TRANSIENT EMISSIONS ESTIMATOR
VRG Controls Transient Emissions Estimator
SUPPLY PRESSURE |  | PSIG | 125
POSITION DELTA |  | (%) | 1%
FREQUENCY |  | (sec) | 30 |  |  |  | ver 060921
mgarvey
RHPA TYPE | RHPA BORE | RHPA STROKE | RHPA VOLUME | DELTA VOLUME | DELTA VOLUME (STD) | TRANSIENT EMISSIONS | ANNUAL TRANSIENT EMISISONS
(--) | (in) | (in) | in^3 | in^3 | SCF | SCFH | MSCFH PER YR
DA | 5 | 4 | 78.5 | 0.785 | 0.0038855 | 0.46626 | 4.0844
DA | 6 | 6 | 169.56 | 1.6956 | 0.0083927 | 1.0071 | 8.8224
DA | 8 | 6 | 301.44 | 3.0144 | 0.01492 | 1.7904 | 15.6843
DA | 8 | 8 | 401.92 | 4.0192 | 0.019894 | 2.3873 | 20.9123
DA | 10 | 6 | 471 | 4.71 | 0.023313 | 2.7976 | 24.5067
DA | 10 | 8 | 628 | 6.28 | 0.031084 | 3.7301 | 32.6755
DA | 10 | 12 | 942 | 9.42 | 0.046626 | 5.5951 | 49.0133
DA | 12 | 12 | 1356.48 | 13.5648 | 0.067142 | 8.057 | 70.5792
DA | 14 | 12 | 1846.32 | 18.4632 | 0.091387 | 10.9665 | 96.0661
DA | 14 | 14 | 2154.04 | 21.5404 | 0.10662 | 12.7942 | 112.0771
SR | 5 | 4 | 78.5 | 0.785 | 0.0038855 | 0.23313 | 2.0422
SR | 6 | 6 | 169.56 | 1.6956 | 0.0083927 | 0.50356 | 4.4112
SR | 8 | 6 | 301.44 | 3.0144 | 0.01492 | 0.89522 | 7.8421
SR | 8 | 8 | 401.92 | 4.0192 | 0.019894 | 1.1936 | 10.4562
SR | 10 | 6 | 471 | 4.71 | 0.023313 | 1.3988 | 12.2533
SR | 10 | 8 | 628 | 6.28 | 0.031084 | 1.865 | 16.3378
SR | 10 | 12 | 942 | 9.42 | 0.046626 | 2.7976 | 24.5067
SR | 12 | 12 | 1356.48 | 13.5648 | 0.067142 | 4.0285 | 35.2896
SR | 14 | 12 | 1846.32 | 18.4632 | 0.091387 | 5.4832 | 48.0331
SR | 14 | 14 | 2154.04 | 21.5404 | 0.10662 | 6.3971 | 56.0386
Notes
Position Delta Equals Magnitude of Valve Position Change as Percent Full Travel
Frequency Equals How Often Control Valve Position Changes
RHPA Type "DA" Equal Double Acting
RHPA Type "SR" Equal Spring Return
Transient Emissions Calcs are Independent of SR Spring Return Cartidge Model
For "D" Dual Actuators Multiply Above Results X2
Temperature Assumed 60F
Enter Data for RED TEXT ONLY
Above Results do NOT include STEADY STATE EMISSIONS
Contact VRG Controls Toll Free +844-FLOW-VRG (sales@vrgcontrols.com) for assistance